## ABB1600
Transformer Losses-Regulation-Efficiency Calcualation
:Three Phase Transformer Detail: |  |  | :I²R Losses Calculation:
Transformer Make | ABB |  | HV Full load current : |  | 0.8798 | Amps
Transformer Serial No | 546619 |  | LV Full load current : |  | 22.5314 | Amps
KVA rating of Transformer | 16000 | VA | HV Side I2R losses |  | 250.0123 | Watts
Primary voltage | 10500 | Volts | LV Side I²R losses |  | 166.8895 | Watts
Secondary voltage | 410 | Volts | Total I² R lossses @ Amb temp |  | 416.9018 | Watts
Primary side Connection |  |  | Total Stray losses @ Amb temp |  | -22.9018 | Watts
Scondary side Connection |  |  | I² R lossses @75° c temp |  | 487.6965 | Watts
No load losses | 1311 | Watts | Stray losses @ 75° c temp |  | -19.5774 | Watts
No load current | 0.59 | Amps | Total Full load losses at @75° c |  | 468.1191 | Watts
Full load losses | 394 | Watts | Total Impedance at ambient temp |  | 944.9446 | Ohms
Impedance voltage | 480 | Volts | Total Resistance at amb temp |  | 538.6023 | Ohms
Lv resistance in milli ohms | 219.16 | M Ohms | Total Reactance (X) : |  | 776.4199 | Ohms
Hv resistance in ohms | 215.33 | Ohms | Resistance at@ 75° c |  | 630.0631 | Ohms
Amb temperature | 30 | Deg c | Impedance at 75° c |  | 999.9036 | Ohms
Total Connected Load on Transformer | 10000 | VA | Percentage Impedance |  | 4.8376 | %
% Loading of Transformer | 62.5% |  | Percentage Resistance |  | 3.0483 | %
|  |  | Percentage Reactance |  | 3.7564 | %
Jignesh.Parmar |  |  | :Regulation Calculation:
www.electricalnotes.wordpress.com |  |  | Regulation at P.F of | Unity | 3.0483
|  |  | Regulation at P.F of | 0.8 | 4.7166 |  | 0.6
:Efficiency Calculation:
|  |  | Efficiency at P.F of | Unity
|  |  | At Transformer Loading | 125% | 91.0647 | %
|  |  | At Transformer Loading | 100% | 90.2532 | %
|  |  | At Transformer Loading | 75% | 88.5903 | %
|  |  | At Transformer Loading | 50% | 84.9688 | %
|  |  | At Transformer Loading | 25% | 74.9477 | %
|  |  | Efficiency at P.F of | 0.8
|  |  | At Transformer Loading | 125% | 92.392 | %
|  |  | At Transformer Loading | 100% | 88.1063 | %
|  |  | At Transformer Loading | 75% | 86.1334 | %
|  |  | At Transformer Loading | 50% | 81.8914 | %
|  |  | At Transformer Loading | 25% | 70.5303 | %
Formulas
HV Full load current = VA / (1.732xVolt)
LV Full load current = VA / (1.732xVolt)
HV Side I2R losses = I²R x1.5
LV Side I²R losses = I²R x0.5x3
Total I² R lossses @ Amb temp = Hv losses+ Lv losses
Total Stray losses @ Amb temp =Measured losses -I² R losses
I² R lossses @75° c temp = ((225+75) x losses) / (225+ Amb temp) |  | .
Stray losses @ 75° c temp=((225+Amb temp)(Stray losses at amb)) / 300
Total Full load losses at @75° c = I²R losses at 75°c+Stray losses at 75°c
Total Impedance at ambient temp =(Imp voltage x1.732) / Full load current
Total Resistance at amb temp = I²R losses / I²
Total Reactance (X) =SQRT(Impedance ²- Resitance ²)
Resistance at@ 75° c =(300 x resistance at amb ) /(225+Amb temp)
Impedance at 75° c =SQRT(R² at 75 + X²)
Percentage Impedance =(Z at 75° c x I x 100)/V1
Percentage Resistance =( R 75° c x I x 100)/V1
Percentage Reactance =(X x I x 100) / V1
Regulation at Unity P.F =(%R cosø+%Xsinø) |  | .
Regulation at 0.8 p.f.= (%R cosø+%Xsinø)+1/200(%R sinø-%Xcosø)2"
Efficiency at Unity P.F
At 125 % of Transformer Loading =(Kva x 1.25 x 100)/((kva x 1.25)+(I²R losses x 1.25²)+(No Load Losses))
Efficiency at 0.8 P.F
At 125 % of Transformer Loading =(Kva x 1.25xp.f x 100)/((kva xp.fx 1.25)+(I²R losses x 1.25²)+(No Load Losses))

## Sheet1
Transformer Losses-Regulation-Efficiency Calcualation
:Three Phase Transformer Detail: |  |  | :I²R Losses Calculation:
Transformer Make |  |  | HV Full load current : |  | 0.83981 | Amps
Transformer Serial No |  |  | LV Full load current : |  | 21.3346 | Amps
KVA rating of Transformer | 16000 | VA | HV Side I2R losses |  | 227.8005 | Watts
Primary voltage | 11000 | Volts | LV Side I²R losses |  | 149.6308 | Watts
Secondary voltage | 433 | Volts | Total I² R lossses @ Amb temp |  | 377.4313 | Watts
Primary side Connection |  |  | Total Stray losses @ Amb temp |  | 16.5687 | Watts
Scondary side Connection |  |  | I² R lossses @75° c temp |  | 441.5234 | Watts
No load losses | 72 | Watts | Stray losses @ 75° c temp |  | 14.1636 | Watts
No load current | 0.59 | Amps | Total Full load losses at @75° c |  | 455.687 | Watts
Full load losses | 394 | Watts | Total Impedance at ambient temp |  | 989.9419 | Ohms
Impedance voltage | 480 | Volts | Total Resistance at amb temp |  | 535.1543 | Ohms
Lv resistance in milli ohms | 219.16 | M Ohms | Total Reactance (X) : |  | 832.8234 | Ohms
Hv resistance in ohms | 215.33 | Ohms | Resistance at@ 75° c |  | 626.0296 | Ohms
Amb temperature | 30 | Deg c | Impedance at 75° c |  | 1041.8771 | Ohms
Total Connected Load on Transformer | 10000 | VA | Percentage Impedance |  | 4.5928 | %
% Loading of Transformer | 62.5% |  | Percentage Resistance |  | 2.7597 | %
|  |  | Percentage Reactance |  | 3.6713 | %
Jignesh.Parmar |  |  | :Regulation Calculation:
www.electricalnotes.wordpress.com |  |  | Regulation at P.F of | Unity | 2.7597
|  |  | Regulation at P.F of | 0.8 | 4.4335 |  | 0.6
:Efficiency Calculation:
|  |  | Efficiency at P.F of | Unity
|  |  | At Transformer Loading | 125% | 96.7973 | %
|  |  | At Transformer Loading | 100% | 97.2678 | %
|  |  | At Transformer Loading | 75% | 97.6856 | %
|  |  | At Transformer Loading | 50% | 97.9629 | %
|  |  | At Transformer Loading | 25% | 97.666 | %
|  |  | Efficiency at P.F of | 0.8
|  |  | At Transformer Loading | 125% | 99.5155 | %
|  |  | At Transformer Loading | 100% | 96.6079 | %
|  |  | At Transformer Loading | 75% | 97.1237 | %
|  |  | At Transformer Loading | 50% | 97.4665 | %
|  |  | At Transformer Loading | 25% | 97.0995 | %
Formulas
HV Full load current = VA / (1.732xVolt)
LV Full load current = VA / (1.732xVolt)
HV Side I2R losses = I²R x1.5
LV Side I²R losses = I²R x0.5x3
Total I² R lossses @ Amb temp = Hv losses+ Lv losses
Total Stray losses @ Amb temp =Measured losses -I² R losses
I² R lossses @75° c temp = ((225+75) x losses) / (225+ Amb temp) |  | .
Stray losses @ 75° c temp=((225+Amb temp)(Stray losses at amb)) / 300
Total Full load losses at @75° c = I²R losses at 75°c+Stray losses at 75°c
Total Impedance at ambient temp =(Imp voltage x1.732) / Full load current
Total Resistance at amb temp = I²R losses / I²
Total Reactance (X) =SQRT(Impedance ²- Resitance ²)
Resistance at@ 75° c =(300 x resistance at amb ) /(225+Amb temp)
Impedance at 75° c =SQRT(R² at 75 + X²)
Percentage Impedance =(Z at 75° c x I x 100)/V1
Percentage Resistance =( R 75° c x I x 100)/V1
Percentage Reactance =(X x I x 100) / V1
Regulation at Unity P.F =(%R cosø+%Xsinø) |  | .
Regulation at 0.8 p.f.= (%R cosø+%Xsinø)+1/200(%R sinø-%Xcosø)2"
Efficiency at Unity P.F
At 125 % of Transformer Loading =(Kva x 1.25 x 100)/((kva x 1.25)+(I²R losses x 1.25²)+(No Load Losses))
Efficiency at 0.8 P.F
At 125 % of Transformer Loading =(Kva x 1.25xp.f x 100)/((kva xp.fx 1.25)+(I²R losses x 1.25²)+(No Load Losses))