## Transformer Fault Current
Transformer Fault Current Calculation
Transformer Impedance
Transformer Impedance is measured in Percent Impedance, this is the Percentage of Rated Primary
Voltage applied to the Transformer's primary winding in order for the rated secondary Full Load Current to
flow in the secondary winding (this test is preformed with the primary winding connected to a Variac
or variable supply and the secondary winding shorted-out).
Transformer Impedance values may vary but typically Blakley Electrics transformers will be between
4 to 5% of primary Voltage. For further details please contact Blakley Electrics' Technical department.
Impedance Voltage Vz = |  |  | Primary Volts V x Percent Impedance Z%
100
Click-On Cells with Blue Text to Modify Values, Results will be Displayed in Green
Any Warnings will be Displayed in Red and Full Results are Displayed Below.
|  |  | Primary Volts (V) | 10000 | Vp
|  |  | Secondary Volts (V) | 400 | Vs
|  |  | Transformer Rating (VA) | 1000 | VA
|  |  | Transformer Configuration | Three
|  |  | Percent Impedance (Z%) | 6 | Z%
| Impedance Voltage (Vz) |  |  | 600
Transformer Maximum Fault Current
|  |  | Transformer Secondary Fault Type | Line to Earth
Maximum Fault Current A= |  |  | 100 |  | x Secondary Full Load Current I
Impedance Volts Vz%
|  |  | Maximum Fault Current (A) | 23.3333
|  |  | Maximum Fault Current (kA) | 0.023333 | 1.4434 | Secondary Current (I)
This is the Maximum Current that can be achieved at the Transformer's Secondary Terminals and
doesn’t allow for any Impedance in the primary or secondary circuitry to and from the transformer.
Transformer Maximum Fault Current Allowing for Loop Impedance
To Calculate the Maximum Fault Current that can be achieved in a circuit fed by a transformer
we refer to the below formula. This formula calculates the loop impedance at the end of a circuit fed
from the secondary winding of a transformer.
When calculating Fault Loop Impedance Select the Correct Transformer Type Above.
Three Phase Transformers Divide the Values for Vs secondary Voltage by √3 and the VA by 3
For Centre Tapped to Earth (CTE) transformers halve the values for Vs and VA .
For RLV / 110V CTE Disconnection Times & Zs figures refer to BS7671:2008, 411.8 Table 41.6
| Zsec = Zp x |  | Vs ² Vp | Z% | Vs² | + (R1 + R2)
|  |  |  | 100 | VA
0.46 | Ω | Zp = Loop impedance of primary circuit including Source (Ze + 2R1)
10000 | V | Vp = Primary Voltage
230.9 | V | Vs = Secondary Voltage
333 | VA | VA = Transformer Rating
6 | % | Z% = Transformer percentage Impedance
0.2 | Ω | (R1 + R2) = Resistance of Secondary circuit Phase and Protective conductor
|  |  | Primary Circuit Impedance (Ze + 2R1) | 0.46 | Zp (Ze + 2R1) Ohms
|  |  | Secondary Circuit Impedance (R1 + R2) | 0.2 | (R1 + R2) Ohms
|  |  | Total Impedance (Zsec) | 9.8065 | Ohms
Transformer Actual Earth Fault Current
To calculate the Actual Fault Current in a transformer we can refer to the below formula taken from
BS7671:2008, 411.4.5 and use the above figure for the transformers Total Impedance (Zsec).
Earth Fault loop Impedance Zs = |  |  | Voltage to Earth Uo |  | Fault Current Ia = |  | Voltage to Earth Uo
|  |  | Fault Current Ia |  |  |  | Loop Impedance Zs
|  |  | Actual Secondary Fault Current (Ia) | 23.5456 | Amps
Primary Fault Current I = |  |  | Secondary Fault Current Ia x |  |  | Secondary Voltage Vs
Primary Voltage Vp
|  |  | Actual Primary Fault Current (I) | 0.94163 | Amps
Blakley calculator (version 2.0) Blakley Electrics Ltd.